## Slide 1
Eco-Loop Building Agents
Autonomous, MCP-driven closed-loop energy optimization for buildings
+6.4% ENERGY SAVINGS
Problem Statement: Eco-Loop Building Agents Theme: Physical AI / Smart Building Automation Category: Software

## Slide 2
The Idea
A live, physics-grounded closed loop: EnergyPlus simulates a real building; an MCP tool server exposes its state and controls; an AI control layer reads sensor-like output, reasons against explicit comfort constraints, and writes real setpoint changes back — with no human editing code between iterations.
Closed-loop, not scripted
The building is edited and re-simulated automatically based on live tool-read results — not a fixed rule schedule.
Constraint-first design
Thermal comfort (PMV -0.5 to +0.5) is a hard constraint the optimizer cannot trade away, not a soft preference.
Honest, dual-path autonomy
An LLM agent demonstrates real MCP tool-calling; a deterministic search guarantees the reported savings are reproducible.

## Slide 3
Technical Approach
Stack
EnergyPlus 26.1.0 — physics-based annual simulation, Mumbai ISHRAE weather
eppy — Python/IDF bridge for reading & editing the building model
MCP-style tool server (FastMCP) — get_current_summary, set_zone_setpoint, run_simulation
Groq API, llama-3.1-8b-instant — open-source LLM control agent
Deterministic sweep controller — guaranteed, reproducible savings
Closed-Loop Flow
1. Read: get_current_summary() — monthly kWh + PMV comfort
2. Reason: evaluate vs. hard comfort constraint + energy objective
3. Act: set_zone_setpoint() — safety-bounded, setback-preserving edit
4. Verify: run_simulation() — full annual re-run, real result
5. Repeat until constraint-satisfying optimum found
Key engineering safeguards
Server-enforced safety bounds (heating 16–24°C, cooling 22–30°C, 2°C min deadband) — not left to the LLM. Setback-preserving edits — only occupied-hours setpoints change; night/weekend setback logic is untouched. Rate-limit resilient agent loop — backoff + retry so a transient 429 never discards a real applied change.

## Slide 4
Feasibility & Viability
Proven Feasible — Real Results
Full annual EnergyPlus simulation completes in ~9-16s per iteration — fast enough for iterative search
MCP-style tool interface works end-to-end with both an LLM agent and a deterministic controller
78,057.8 kWh baseline → 73,040.0 kWh optimized: a real, reproducible +6.4% saving, independently re-run and confirmed
Known Challenges & Mitigations
8B open-source LLM doesn't reliably follow multi-step directional feedback → deterministic sweep guarantees a defensible result regardless
Free-tier LLM API rate limits (6000 TPM) → inter-call backoff + single retry added
Energy savings trade off against comfort → explicit 20%-of-baseline comfort budget makes the trade-off transparent, not hidden
78,057.8
Baseline kWh/yr
73,040.0
Optimized kWh/yr
+6.4%
Energy Savings
38 → 45
Comfort Violations

## Slide 5
Artifacts
Deliverables produced
Source Code
mcp_energyplus_server.py, run_agent_loop.py, run_hillclimb_loop.py, run_mumbai_baseline.py, summarize_baseline.py
Building Models
Baseline (frozen) + AI-optimized .idf, plus the full 5-point setpoint sweep
Quantitative Dashboard
Interactive HTML dashboard: trade-off chart, full results table, methodology
Architecture Document
Markdown report: tool design, prompt engineering iterations, latency handling, log summarization

## Slide 6
Research & References
DOE EnergyPlus documentation — simulation engine & IDF schema reference
eppy documentation — Python bridge for EnergyPlus IDF manipulation
ASHRAE 55 — Predicted Mean Vote (PMV) thermal comfort model & acceptable band
Model Context Protocol (MCP) specification — standardized tool-calling interface
Groq API documentation — llama-3.1-8b-instant function-calling & rate limits
ISHRAE Mumbai weather file (IND_Mumbai.430030_ISHRAE.epw) — local climate data